www.rs485.com

Phone: 513-874-4796    Fax: 513-874-1236

PRELIMINARY INFORMATION

PF8R OPERATION GUIDE

PF8R RS485/RS232 SERIAL REMOTE RELAY BOARD

(Software Version 1.5A, April 1, 2006)

Document Date: 01/06/2007

Table Of Contents

INTRODUCTION	2

Figure 1. PF8R	2

COMMAND STRUCTURE	3

Table 1: USER COMMANDS	3

Table 2: USER COMMANDS (CONTINUED)	4

Table 3: RS232/RS485 CONFIGURATION	5

Table 5: TABLE OF SPECIFICATIONS FOR COMMON COMMUNICATIONS STANDARDS	7

Figure 2: COMPONENT SCREEN	8

# INTRODUCTION

The PF8R Remote Relay Board has 8 relay outputs.  The unit can be controlled by our simple/efficient command structure from a host computer (computer mode), such as a PC with standard firmware. The unit can communicate using RS485 or RS232, at data rates up to 115.2K bits/second. The PF-series devices have a unique feature being field upgraded to new or custom versions of firmware while installed in a network.

The PF8R has an on board switching regulator for 9-35VDC (7.5W) operation, LED indicators monitor data flow of the serial port and relay status. 22 jumpers for communications address, Baud rate, mode control, etc.

## Figure 1. PF8R

# COMMAND STRUCTURE

All commands begin with the command start character ‘*’ next is a three character op-code followed by the parameter list encased in parentheses.  The first parameter will always be the unit address, which for this unit settable to 00H through FFH using jumpers J16(msb)-J23(lsb).

USER COMMANDS

Important Note! Table below assumes the address set on J16(msb)-J23(lsb) is set to 0FH or J20,J21,J22, and J23 installed.  Also, in the table any variable input is shown in lowercase, the user would provide uppercase hexadecimal encoded characters in place of the lowercase input.

## Table 1: USER COMMANDS

| COMMAND FORMAT | RESPONSE FORMAT | DESCRIPTION / NOTES |
| --- | --- | --- |
| *LOC(0FH) | LUNIT(0FH,F)-0000# | LOCATE COMMAND (0FH – UNIT ADDRESS SET WITH J16-J23). RETURNS PF8R FLAGS CURRENTLY RETURNS 0000, RESERVED FOR FUTURE DEVELOPMENT |
| *GET(0FH) | GUNIT(0FH,I,O,J)-0000-00XX-0000# | GET I/O STATUS (I,O,J)-INPUTS,OUTPUTS,JUMPERS. XX – HEX ENCODED STATUS OF THE 8 RELAYS |
| *KXX(0FH,AAH,mmH) | KSTAT-00XX# | mm – HEX ENCODED MASK OF DESIRED OUTPUT CONFIGURATION, RELAYS ARE ACTIVATED/DEACTIVATED UNTIL COMMANDED OTHERWISE. XX – HEX ENCODED STATUS OF THE 8 RELAYS AFTER COMMAND EXECUTION |
| *KXX(0FH,kkH,ttttH) | KSTAT-00XX# | RELAY NUMBER kk=01..08 IS ACTIVATED FOR HEX ENCODED TIME (tttt) * 100MS PER COUNT |
| *KAT(0FH,mmH,ttttH) | KSTAT-00XX# | ALL RELAYS TIMED COMMAND WITH MASK, 8 BIT ASCII HEX MASK mmH IS USED 1 BIT PER RELAY K8(msb)-K1(lsb) TO ACTIVATE WHEN BIT IS 1 FOR THE HEX ENCODED TIME (tttt) * 100MS PER COUNT, WHEN THE MASK BIT ASSOCIATED WITH RELAY IS ZERO THE RELAY TIMER IS CLEARED AND THE RELAY IS DEACTIVATED. |
| *KAX(0FH,mmH,ttttH) | KSTAT-00XX# | ALL RELAYS TIMED COMMAND WITH MASK, 8 BIT ASCII HEX MASK mmH IS USED 1 BIT PER RELAY K8(msb)-K1(lsb) TO ACTIVATE WHEN BIT IS 1 FOR THE HEX ENCODED TIME (tttt) * 100MS PER COUNT, WHEN THE MASK IS ZERO THE ASSOCIATED RELAY IS UNAFFECTED. |

## Table 2: USER COMMANDS (CONTINUED)

| COMMAND FORMAT | RESPONSE FORMAT | DESCRIPTION / NOTES |
| --- | --- | --- |
| *IOR(0FH) | IOREAD(0FH,I,O)-0000-00XX# | READ THE INPUT/OUTPUT STATUS, XX HEX ENCODED STATUS OF THE 8 RELAYS K1-K8 |
| *OPT(0FH) | OPTIONS-0FH TDLY-TX DELAY=dddd (*500uS) | READ THE USER CONFIGURABLE OPTIONS |
| *OPT(0FH,TDLY=dd) | OPTIONS(0FH,TRANSMIT DELAY=dd)# | FOR RS485 A MINIMUM DELAY OF DECIMAL 0-255 (*500uS) BEFORE THE COMMAND RESPONSE IS TRANSMITTED |
| *VER(0FH) | VER-1.5A-20060401# | RETURNS THE FIRMWARE VERSION STRING |
| *TYP(0FH) | TYPE-PF8R-REV-B# | RETURNS THE UNIT TYPE STRING |
| *TST(0FH) | 0000-00XX-0000-0000# | TEST COMMAND RETURNS THE STATE OF THE OUTPUTS XX ASCII HEX ENCODED VALUE. OTHER VALUES ARE DONT CARE FOR THIS PRODUCT. |
| *TMR(0FH) | TIMERS(0FH, 1:XXXX 2:XXXX 3:XXXX 4:XXXX 5:XXXX 6:XXXX 7:XXXX 8:XXXX | RETURNS THE CURRENT COUNT IN A HEX ENCODED STRING FOR ALL 8 TIMERS CONTROLLING THE 8 RELAYS |

CONFIGURATION TABLES

Notes and abbreviations:

I = Install jumper (JX), R = Remove Jumper (JX),

TX = Transmit, RX = Receive, * = Factory Default Setting,

HW = Hardware Setup, SW = Software Setup.

## Table 3: RS232/RS485 CONFIGURATION

| JX | MODE | JUMPER FUNCTION AND NOTES |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| J1-4 | HW | J1 | J2 | J3 | J4 | RS-232 Port Configuration |
|  |  | I* | I* | R | R | Computer Mode |
|  |  | R | R | I | I | Modem Mode |
| J5 | HW | RS485 Speed up install for baud rates above 38400 |  |  |  |  |
| J6 | HW | A – RS-232, B* – RS-485 |  |  |  |  |
| J7 | HW | Special binary relay control function*1 enabled if installed. |  |  |  |  |
| J8 | HW | Reserved |  |  |  |  |
| J9 | HW | Ground mounting post if installed |  |  |  |  |
| J10 | SW | Monitor Mode if removed, if removed on power up baud is fixed to 9600 otherwise baud is jumper selected. |  |  |  |  |
| J11-J14 | SW | Baud Rate Selection Jumpers See Table 2. |  |  |  |  |
| J15 | HW | Reserved |  |  |  |  |
| J16-J23 | SW | External Address (J16-msb : J23-lsb) |  |  |  |  |

*1 – If enabled, with J7 installed, sending the 8bit binary code equal to 2n-1 enables relay Kn for 5 seconds. If before 5 seconds the unit receives the 8bit binary code equal to 2n-1 the time is reset to 5 seconds for relay Kn to be enabled.  Example: Send binary 01 activates relay K1, send binary 128 activates relay K8, etc. Note this mode disables all commands of the normal command structure, to re-flash new firmware the jumper on J7 must be removed prior to re-flashing.

Table 4: RS-232 BAUD RATE SETUP

| Baud Rate Selection in any MODE (J11 – J14) Note: Sampled on power-up only! |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| HEX | J11 | J12 | J13 | J14 | Baud |
| F | I* | I* | I* | I* | 9600 |
| E | I | I | I | R | 115.2K |
| D | I | I | R | I | 9600 |
| C | I | I | R | R | 57.6K |
| B | I | R | I | I | 38.4K |
| A | I | R | I | R | 28.8K |
| 9 | I | R | R | I | 19.2K |
| 8 | I | R | R | R | 14.4K |
| 7 | R | I | I | I | 9600 |
| 6 | R | I | I | R | 4800 |
| 5 | R | I | R | I | 2400 |
| 4 | R | I | R | R | 9600 |
| 3 | R | R | I | I | 9600 |
| 2 | R | R | I | R | 9600 |
| 1 | R | R | R | I | 9600 |
| 0 | R | R | R | R | 9600 |

## Table 5: TABLE OF SPECIFICATIONS FOR COMMON COMMUNICATIONS STANDARDS

| SPECIFICATIONS |  |  | RS232 |  | RS423 |  | RS422 |  | RS485 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Mode of Operation |  |  | SINGLE-ENDED |  | SINGLE-ENDED |  | DIFFER- ENTIAL |  | DIFFER- ENTIAL |
| Total Number of Drivers and Receivers on One Line |  |  | 1 DRIVER 1 RECVR |  | 1 DRIVER 1 RECVR |  | 10 DRIVER 10 RECVR |  | 32 DRIVER 32 RECVR |
| Maximum Cable Length |  |  | 50 FT. |  | 4000 FT. |  | 4000 FT. |  | 4000 FT. |
| Maximum Data Rate |  |  | 20kb/s |  | 100kb/s |  | 10Mb/s |  | 10Mb/s |
| Maximum Driver Output Voltage |  |  | ±25V |  | ±6V |  | -0.25V to +6V |  | -7V to +12V |
| Driver Output Signal Level (Loaded Min.), (Unloaded Max.) | Loaded | ±5V to ±15V |  | ±3.6V |  | ±2.0V |  | ±1.5V |  |
|  | Unloaded | ±25V |  | ±6V |  | +/-6V |  | ±6V |  |
| Driver Load Impedance (Ohms) |  |  | 3k to 7k |  | >=450 |  | 100 |  | 54 |
| Max. Driver Output Current in High Impedance State | Power On | N/A |  | N/A |  | N/A |  | ±100uA |  |
|  | Power Off | ±6mA @ ±2v |  | ±100uA |  | ±100uA |  | ±100uA |  |
| Slew Rate (Max.) |  |  | 30V/uS |  | Adjustable |  | N/A |  | N/A |
| Receiver Input Voltage Range |  |  | ±15V |  | ±12V |  | -10V to +10V |  | -7V to +12V |
| Receiver Input Sensitivity |  |  | ±3V |  | ±200mV |  | ±200mV |  | ±200mV |
| Receiver Input Resistance (Ohms) |  |  | 3k to 7k |  | 4k min. |  | 4k min. |  | >=12k |

## Figure 2: COMPONENT SCREEN