# www.rs485.com

# Phone: 513-874-4796    Fax: 513-874-1236

PRELIMINARY INFORMATION

PF8R OPERATION GUIDE

PF8R RS485/RS232 SERIAL REMOTE RELAY BOARD

(Software Version xxxx, November 2, 2003)

INTRODUCTION

The PF8R Remote Relay Board has 8 relay outputs.  The unit can be controlled by our simple/efficient command structure from a host computer (computer mode), such as a PC with standard firmware. The unit can communicate using RS485 or RS232, at data rates up to 115.2K bits/second. The PF-series devices have a unique feature being field upgraded to new or custom versions of firmware while installed in a network.

The PF8R has an onboard switching regulator for 9-35VDC (7.5W) operation, LED indicators monitor data flow of the serial port and relay status. 22 jumpers for communications address, Baud rate, mode control, etc.

## Figure 1. PF8R

PRELIMINARY COMMAND STRUCTURE FOR 
THE PF8R UNIT AND OTHER PFxxxxx I/O BOARDS

(UPDATED 10-31-03)

COMMAND		RESPONSE (X=NIBBLE)				NOTES

*LOC(0FH)	LUNIT(0FH)-XXXX#<CR><LF>		XXXX=FLAGS

*GET(0FH)	GUNIT(0FH)-XXXX-IIII-OOOO-JJJJ#<CR><LF>

X=FLAGS

I=INPUTS

O=OUTPUTS

J=JUMPERS

*VER(0FH)	VER-2.1A-20030921<CR><LF>		VERSION AND DATE CODE

*TYP(0FH)	TYPE-PFAHUB-REV-A<CR><LF>		TYPE AND REVISION

*HLP(0FH)	DISPLAY HELP PAGE<CR><LF>		DISPLAY HELP PAGE

-------------------- I/O BOARD COMMANDS -----------------

*KXX(0FH,AAH,XXXXH)	KALL-XXXX<CR><LF>	XXXX=BIT PATTERN (HEX)

(ADDRESS, ALL RELAYS, MASK VALUE)		NOTE: TERMINATE ALL TIMERS

*KXX(0FH,01H,XXXXH)	K01-DDDD<CR><LF>	DDDD=TIME (HEX) 0.1SEC.

(ADDRESS, RELAY#, TIMER)			0000H=OFF, FFFFH=ON

*KXX(0FH,01H,XXXH)		"			"

*KXX(0FH,01H,XXH)			"			"

*KXX(0FH,01H,XH)			"			"

----------------------------------------------------------

Command: *OPT(0FH, READ)

Response: OPTIONS(0FH,TDLY=01H)

Description: Read the non-volatiel options

Command: *OPT(0FH, TDLY, 01H)

Response: OPTIONS(0FH,TDLY=01H)

Description: Set the transmit delay increments of 50us per count

Configuration Tables

Notes and abbreviations:

I = Install jumper (JX), R = Remove Jumper (JX), XX = don’t care,

M/S = Master or Slave Mode, M = Master Mode, S = Slave Mode,

TX = Transmit, RX = Receive, * = Factory Default Setting,

HW = Hardware Setup.

Table 1: RS232/RS485 Configuration

| JX | MODE | #### JUMPER FUNCTION AND NOTES |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| J1-4 | ## HW | J1 | J2 | J3 | J4 | RS-232 Port Configuration |
|  |  | I* | I* | R | R | Computer Mode |
|  |  | R | R | I | I | Modem Mode |
| J5 | ## HW | RS485 Speed up install for baud rates above 38400 |  |  |  |  |
| J6 | ## HW | A – RS-232, B* – RS-485 |  |  |  |  |
| J7 | ## SW | Boot loader on power up if installed. |  |  |  |  |
| J8 | ## SW | Reserved |  |  |  |  |
| J9 | ## HW | Ground mounting post if installed |  |  |  |  |
| J10 | ## SW | Monitor Mode if removed, if removed on power up baud is fixed to 9600 otherwise baud is jumper selected. |  |  |  |  |
| J11-J14 | ## SW | Baud Rate Selection Jumpers See Table 2. |  |  |  |  |
| J15 | ## SW | Reserved |  |  |  |  |
| J16-J23 | ## SW | External Address (J16-msb : J23-lsb) |  |  |  |  |

Table 2: RS-232 BAUD RATE SETUP

| Baud Rate Selection in any MODE (J20 – J23) Note: Sampled on power-up only! |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| HEX | J11 | J12 | J13 | J14 | Baud |
| F | I* | I* | I* | I* | 9600 |
| E | I | I | I | R | 115.2K |
| D | I | I | R | I | 9600 |
| C | I | I | R | R | 57.6K |
| B | I | R | I | I | 38.4K |
| A | I | R | I | R | 28.8K |
| 9 | I | R | R | I | 19.2K |
| 8 | I | R | R | R | 14.4K |
| 7 | R | I | I | I | 9600 |
| 6 | R | I | I | R | 4800 |
| 5 | R | I | R | I | 2400 |
| 4 | R | I | R | R | 9600 |
| 3 | R | R | I | I | 9600 |
| 2 | R | R | I | R | 9600 |
| 1 | R | R | R | I | 9600 |
| 0 | R | R | R | R | 9600 |

Table 6: TABLE OF SPECIFICATIONS FOR COMMON COMMUNICATIONS STANDARDS:

| SPECIFICATIONS |  | RS232 | RS423 | RS422 | RS485 |
| --- | --- | --- | --- | --- | --- |
| Mode of Operation |  | SINGLE-ENDED | SINGLE-ENDED | DIFFER- ENTIAL | DIFFER- ENTIAL |
| Total Number of Drivers and Receivers on One Line |  | 1 DRIVER 1 RECVR | 1 DRIVER 1 RECVR | 10 DRIVER 10 RECVR | 32 DRIVER 32 RECVR |
| Maximum Cable Length |  | 50 FT. | 4000 FT. | 4000 FT. | 4000 FT. |
| Maximum Data Rate |  | 20kb/s | 100kb/s | 10Mb/s | 10Mb/s |
| Maximum Driver Output Voltage |  | ±25V | ±6V | -0.25V to +6V | -7V to +12V |
| Driver Output Signal Level (Loaded Min.), (Unloaded Max.) | Loaded | ±5V to ±15V | ±3.6V | ±2.0V | ±1.5V |
|  | Unloaded | ±25V | ±6V | +/-6V | ±6V |
| Driver Load Impedance (Ohms) |  | 3k to 7k | >=450 | 100 | 54 |
| Max. Driver Output Current in High Impedance State | Power On | N/A | N/A | N/A | ±100uA |
|  | Power Off | ±6mA @ ±2v | ±100uA | ±100uA | ±100uA |
| Slew Rate (Max.) |  | 30V/uS | Adjustable | N/A | N/A |
| Receiver Input Voltage Range |  | ±15V | ±12V | -10V to +10V | -7V to +12V |
| Receiver Input Sensitivity |  | ±3V | ±200mV | ±200mV | ±200mV |
| Receiver Input Resistance (Ohms) |  | 3k to 7k | 4k min. | 4k min. | >=12k |