# www.rs485.com and/or  www.fiberspace1.com

# Phone: 513-874-4796    Fax: 513-874-1236

PRELIMINARY INFORMATION

STAND ALONE OPERATION OF THE

AT1616L RS485/RS232 SERIAL REMOTE I/O BOARD

(Software Version 02.0B, April 28, 2001)

INTRODUCTION

The AT1616L Remote I/O Board has 16 OPTO-ISOLATED inputs and 16-Relay (Form C) outputs.  The unit can be controlled by our simple/efficient command structure from a host computer (computer mode), such as a PC. Also, two units can be operated in a standalone mode (master/slave mode) to form a "Relay extension cord," with 16-channels of control in each direction, at distances of up to 4000 ft. or more.  The unit can communicate using RS485 or RS232, at data rates up to 115.2K bits/second.

The AT1616L has an onboard switching regulator for 12VDC operation, LED indicators for all inputs and outputs, 18 jumpers for communications address, Baud rate, mode control, etc.  Wago connectors are provided for ease of wire installation/removal.  The RS485 serial port has built in transient protection and jumper selectable termination.  LED indicators monitor the data flow of the serial port.

Jumper Configuration Tables

Notes and abbreviations:

I = Install jumper (JX), R = Remove Jumper (JX), XX = don’t care,

M/S = Master or Slave Mode, M = Master Mode, S = Slave Mode,

TX = Transmit, RX = Receive, * = Factory Default Setting, HW = Hardware Setup.

Table 1: RS232/RS485 Configuration

| JX | MODE | #### JUMPER FUNCTION AND NOTES |
| --- | --- | --- |
| J1 | ## HW | Serial Port DSR Function (RS-232) |
| J2 | ## HW | RS-485 Pin 1 Common |
| J3 | ## HW | RS-485 Pin 6 Common |
| J4 | ## HW | RS-485 Termination (120 OHMS) |
| J5 | ## HW | Processor Reset Select, Do Not Change! |
| J6 | ## HW | A – Green Led RXEN, B* – Green Led RX Data Input |
| J7 | ## NA | RESERVED |
| J8 | ## NA | RESERVED |

##### Table 2: Master/Slave Jumper Setup

| JX | MODE | J9 | J10 | ## J11 | TX retry time-out value |  |
| --- | --- | --- | --- | --- | --- | --- |
| J9 J10 J11 | ## M | I | I | I | 1.0S retransmit delay |  |
|  |  | I | I | R | 0.5S retransmit delay |  |
|  |  | I | R | I | 100mS retransmit delay |  |
|  |  | I* | R* | R* | 10mS retransmit delay |  |
|  |  | R | I | I | 8mS retransmit delay |  |
|  |  | R | I | R | 4mS retransmit delay |  |
|  |  | R | R | I | 2mS retransmit delay |  |
|  |  | R | R | R | 1mS retransmit delay |  |
| J12 J13 ## J14 | ## M/S | J12 | J13 | ## J14 | ### DATA INTEGRITY CONTROL |  |
|  |  | I | I | I | Data same for last 8 RX to change |  |
|  |  | I | I | R | Data same for last 7 RX to change |  |
|  |  | I | R | I | Data same for last 6 RX to change |  |
|  |  | I | R | R | Data same for last 5 RX to change |  |
|  |  | R | I | I | Data same for last 4 RX to change |  |
|  |  | R | I | R | Data same for last 3 RX to change |  |
|  |  | R* | R* | I* | Data same for last 2 RX to change |  |
|  |  | R | R | R | Data updates outputs immediately |  |
| ## J15 | ## XX | RESERVED |  |  |  |  |
| J16 | ## M/S | Master/Slave Selection, I* = MASTER, R = SLAVE |  |  |  |  |
| J17 | ## M/S | I* = EIGHT BIT DATA BETWEEN MASTER AND SLAVE, 3 BYTES FOR BOTH SIDES TO UPDATE R = NINE BIT DATA, 2 BYTES FOR BOTH SIDES TO UPDATE. NOTE! (FUTURE ENHANCEMENT) 8BIT MODE ONLY |  |  |  |  |
| J18 J19 | ## M/S | J19 | J18 | DELAY |  | Programmable Relay dropout if communication loss. Disabled, 1, 2 or 5 seconds. |
|  |  | R | R | No dropout |  |  |
|  |  | R | I | 1 Sec. |  |  |
|  |  | I | R | 2 Sec. |  |  |
|  |  | I* | I* | 5 Sec. |  |  |

Table 3: RS-232 BAUD RATE SETUP

| Baud Rate Selection in any MODE (J20 – J23) Note: Sampled on power-up only! |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| HEX | J20 | J21 | J22 | J23 | Baud |
| F | I* | I* | I* | I* | 9600 |
| E | I | I | I | R | 115.2K |
| D | I | I | R | I | 9600 |
| C | I | I | R | R | 57.6K |
| B | I | R | I | I | 38.4K |
| A | I | R | I | R | 28.8K |
| 9 | I | R | R | I | 19.2K |
| 8 | I | R | R | R | 14.4K |
| 7 | R | I | I | I | 9600 |
| 6 | R | I | I | R | 4800 |
| 5 | R | I | R | I | 2400 |
| 4 | R | I | R | R | 1200 |
| 3 | R | R | I | I | 600 |
| 2 | R | R | I | R | 300 |
| 1 | R | R | R | I | 9600 |
| 0 | R | R | R | R | 9600 |

###### Table 4: Jumpers J24-J30, Hardware Setup

| JX | MODE | #### JUMPER FUNCTION AND NOTES |
| --- | --- | --- |
| J24 | ## XX | Reserved |
| J25 | ## HW | *I – Left Side V- Connected to Board Ground R – Left Side V- Isolated Supplied External |
| J26 | ## HW | A - Left Side Supply V+ Connected to Board +12 *B – Left Side Supply V+ Connected to Board +5 R – Left Side Supply V+ Isolated Supplied External |
| J27 | ## HW | *A – Right Side Supply +12, If J30-A B – Right Side Supply +5, If J30-A R – Right Side Supply External See J30 |
| J28 | ## HW | Reserved |
| J29 | ## HW | A – Right Side V- Isolated Supplied External *B – Right Side V- Connected to Board Ground R – Right Side V- Isolated Supplied External |
| J30 | ## HW | A – Right Side V+ Connected J27-A +12 or J27-B +5 *B – Right Side V+ Connected +5 R – Right Side V+ Isolated Supplied External |

Table 5: TABLE OF SPECIFICATIONS FOR COMMON COMMUNICATIONS STANDARDS:

| SPECIFICATIONS |  | RS232 | RS423 | RS422 | RS485 |
| --- | --- | --- | --- | --- | --- |
| Mode of Operation |  | SINGLE-ENDED | SINGLE-ENDED | DIFFER- ENTIAL | DIFFER- ENTIAL |
| Total Number of Drivers and Receivers on One Line |  | 1 DRIVER 1 RECVR | 1 DRIVER 10 RECVR | 1 DRIVER 10 RECVR | 1 DRIVER 32 RECVR |
| Maximum Cable Length |  | 50 FT. | 4000 FT. | 4000 FT. | 4000 FT. |
| Maximum Data Rate |  | 20kb/s | 100kb/s | 10Mb/s | 10Mb/s |
| Maximum Driver Output Voltage |  | +/-25V | +/-6V | -0.25V to +6V | -7V to +12V |
| Driver Output Signal Level (Loaded Min.), (Unloaded Max.) | Loaded | +/-5V to +/-15V | +/-3.6V | +/-2.0V | +/-1.5V |
|  | Unloaded | +/-25V | +/-6V | +/-6V | +/-6V |
| Driver Load Impedance (Ohms) |  | 3k to 7k | >=450 | 100 | 54 |
| Max. Driver Output Current in High Impedance State | Power On | N/A | N/A | N/A | +/-100uA |
|  | Power Off | +/-6mA @ +/-2v | +/-100uA | +/-100uA | +/-100uA |
| Slew Rate (Max.) |  | 30V/uS | Adjustable | N/A | N/A |
| Receiver Input Voltage Range |  | +/-15V | +/-12V | -10V to +10V | -7V to +12V |
| Receiver Input Sensitivity |  | +/-3V | +/-200mV | +/-200mV | +/-200mV |
| Receiver Input Resistance (Ohms) |  | 3k to 7k | 4k min. | 4k min. | >=12k |